TYPICAL SPECIFICATION

WIZARD® 4000

CHEMICAL DAY TANK SCALE

SPECIFICATION SECTION 11245 - Chemical Feeders

SPECIFICATION SECTION 11240  - Chemical Metering Pumps:

SCALE PLATFORMS:  A quantity of ____chemical scale(s) of ___________ lbs capacity shall be provided and shall be of the digital readout/electronic load cell type.  Scale platform shall be sized to accept a _______inch diameter tank.  Four (4) adjustable hold down lugs shall be furnished on the platform to allow securing the vessel to the platform.   Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light.  Flexible cable shall connect load cell to indicator to allow easy remote installation of the readout.  Cable length shall be _____ feet (20'standard).

INSTRUMENT ENCLOSURE, OUTPUTS & ALARMS:  Indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure.   Indicator shall have a 20 key digital keypad & ability to display 2 scales at a time on a backlit alphanumeric display.  If more than 2 scales are being monitored, display shall automatically scan all scales in the system.   Indicator shall have adjustable 4-20mA signals that output net weight and chemical feed rate for each scale.  Indicator shall display an alarm in any of the following conditions: Low level, high level, low feed rate, high feed rate, max daily use, min daily use, supply exhausted and load cell failure.  An alarm log shall store the most recent 10 alarm conditions with time and date of occurrence.  A quantity of ____ relays (up to 12 per indicator) shall be provided for remote alarm indication or transfer pump control.   Indicator shall be enabled with MODBUS protocol for remote RS-485 serial communications.

DISPLAY & INVENTORY CONTROL SOFTWARE: Keypad and Menu items shall have independent password protection to prevent unauthorized operation.  Both a numerical and a bar graph display shall give operator the ability to monitor chemical by weight, volume or percent full.    Each channel shall have a user selectable, two digit scale ID number and shall display net remaining, pure chemical remaining, feed rate, daily usage, total amount used, days until empty, gross weight and tare weight.    A TANK LOAD key shall pause & project usage accumulation during chemical re-supply to maintain accurate usage data over multiple tank loads.  A data log shall store the DAILY USAGE for each of the previous 31 days.  Indicator re-calibration in the field shall be accomplished through the keypad and shall not require the use of dead weights.

Scale shall carry a Full Five (5) Year Factory Warranty.  “Limited” warranties shall be considered unacceptable.  Full scale accuracy shall be better than ¼ of 1%.   Scale shall be CHEM-SCALE®  with TUF-COATTM Environmental Armor model________ and WIZARD 4000® digital display,  Model __________, as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com).

Model Numbers:

PLATFORM:		Capacity	30" x 30"		40" x 40"		50" x 50"		60" x 60"

1,000 lb.	30-DR10LP

2,000 lb.	30-DR20LP	40-DR20LP

3,000 lb.	30-DR30LP	40-DR30LP

4,000 lb.			40-DR40LP

5,000 lb.					50-DR50LP

6,000 lb.					50-DR60LP	60-DR60LP

8,000 lb.					50-DR80LP	60-DR80LP

10,000 lb.							60-DR100LP

12,000 lb. (Special)						60-DR120LP

Consult factory for other capacities and Metric Model Numbers.

INDICATOR:		4000-1	One Channel

4000-2	Two Channel

4000-3	Three Channel

4000-4	Four Channel

File: _WEB\SPECS\SPCCHMWZ

FORCE FLOW  1-800-893-6723

FAX: 925-686-6713

CHEM/WIZ

09/03/03