TYPICAL SPECIFICATION

SOLO® XT

CHEM-SCALE

SPECIFICATION SECTION 11245 - Chemical Feeders

SPECIFICATION SECTION 11240 - Chemical Metering Pumps

A quantity of ______ day tank scales of______ lb. capacity shall be provided and shall be of the digital readout/hydraulic load cell type.   Each weighing platform shall have a sole and separate weight indicator with no shared components.   Scale platform shall accommodate a _______ inch diameter tank.  Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light.

Scale shall be of the single hydraulic load cell design.  Load cell shall be of the temperature stable, rolling diaphragm type. Flexible hose shall connect load cell to indicator to allow easy remote installation of the digital indicator.  Hose shall be ____ ft. (12 ft standard) in length.

Indicator shall convert the hydraulic load cell signal into a digitally displayed weight value.  Indicator shall be 12 to 36 VDC loop powered (power supply provided by others) with onboard battery back-up.   Indicator shall not require 110 VAC or 220 VAC for operation.  Batteries shall provide approximately 1000 hours of back-up power.  Indicator shall be housed in a NEMA 4X enclosure with 6 function keys for indicator operation.  Net weight shall be displayed in two ways; a numeric display with .81 inch high characters, and an analog 0-100% bar graph display.  A third display line shall prompt the user through routine user operations.

User shall be able to set the net weight either by scrolling in the net chemical weight, or scrolling in the tank tare weight.   A menu key shall provide access to the following 5 functions: 1) Zero indicator;   2) Set bar graph & 4-20mA capacity, 3) Set display auto-off time, 4) Set alarm relay values and 5) Set decimal point

Indicator shall provide a 4-20mA output proportional to Net Weight.   An 18 inch flying lead shall be provided for termination in a user supplied junction box.

OPTIONAL LEVEL ALARM RELAY:

Indicator shall have a 0.5 amp dry contact relay for level alarm.  Set point shall be entered via the keypad and shall be configurable as a high or low level alarm.  An 18 inch flying lead shall be provided for termination in a user supplied junction box.

Scale shall carry a Full Five (5) Year Warranty.   “Limited” Warranties shall be considered unacceptable.

Full scale accuracy shall be better than 1/2 of 1%.    Scale shall be CHEM-SCALETM with TUF-COATTM coating and SOLO XT digital display, Model __-XT__LPMA as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA  94520 USA (800) 893-6723 (www.forceflow.com).